## Sheet2
a | b | c | d | e | f | g | h | i
City of Dayton
| Generator Inspection/Maintenance Log |  |  |  | Date:
Generator:
Inspector:
| Note any corrective actions taken |  | [Weekly, Monthly, Semi-annual, Annual]
| Component |  | Service Frequency Level 1 | Complete | Comment. Recommended Action for next month |  |  | Responsible Party?
Tasks and intervals being checked against O&Ms
Safety
1 | Before beginning any examination or inspection perform required lockout/tagout of equipment. |  | Every Maintenance Visit |  |  |  |  | Contractor
Automatic Transfer Switch
1 | General visual inspection | Visual Inspect | W |  |  |  |  | Dayton
2 | Tighten control and power wiring connections | Check | M |  |  |  |  | Contractor
Electrical Generator Diesel Engine
1 | Fuel | [6 empty] | Dayton
a. | Check main supply tank level and drain water | Check | W |  |  |  |  | Dayton
b. | Day tank level | Visual Inspect / Check | W |  |  |  |  | Dayton
c. | Day tank float switch | Visual Inspect / Test | W |  |  |  |  | Dayton
d. | Supply or transfer pump operation | Visual Inspect / Test | W |  |  |  |  | Dayton
e. | Solenoid valve operation | Visual Inspect / Test | W |  |  |  |  | Dayton
f. | Water in system | Check / Clean | W |  |  |  |  | Dayton
g. | Strainer, fuel filter, dirt leg, water separator, gauze filter, or combination | Clean/Replace | S |  |  |  |  | Contractor
h. | Flexible hose and connectors | Visual Inspect / Replace | A |  |  |  |  | Contractor
i. | Tank vents and overflow piping unobstructed | Check / Clear | A |  |  |  |  | Contractor
j. | Fuel Line Piping | Visual Inspect | A |  |  |  |  | Contractor
2 | Lubrication System
a. | Oil level | Visual Inspect / Fill | W |  |  |  |  | Dayton
b. | Oil change | Change | A |  |  |  |  | Contractor
c. | Oil filter(s) | Change | A |  |  |  |  | Contractor
d. | Lube oil heater | Check | W |  |  |  |  | Dayton
e. | Crankcase breather | Check / Change / Clean | S |  |  |  |  | Contractor
3 | Cooling System
a. | Level | Visual Inspect / Fill | W |  |  |  |  | Dayton
b. | Antifreeze protection level | Test | S |  |  |  |  | Contractor
c. | Change Antifreeze | Change | A |  |  |  |  | Contractor
d. | Adequate cooling water to heat exchanger | Check | W |  |  |  |  | Dayton
e. | Rod out heat exchanger | Clean | A |  |  |  |  | Contractor
f. | Adequate fresh air through radiator | Check | W |  |  |  |  | Dayton
g. | Clean exterior of radiator | Clean | A |  |  |  |  | Contractor
h. | Fan and alternator belt | Visual Inspect / Check | M |  |  |  |  | Contractor
i. | Water pump(s) | Visual Inspect | W |  |  |  |  | Dayton
j. | Condition of flexible hoses and connection | Visual Inspect / Check | W |  |  |  |  | Dayton
k. | Jacket water heater | Check | W |  |  |  |  | Dayton
l. | Inspect duct work, clean louvers | Visual Inspect / Check / Clean | A |  |  |  |  | Contractor
m. | Louver motors and controls | Visual Inspect / Clean / Test | A |  |  |  |  | Contractor
4 | Exhaust System
a. | Leakage | Visual Inspect / Check | W |  |  |  |  | Dayton
b. | Drain condensate trap | Check | W |  |  |  |  | Dayton
c. | Insulation and fire hazards | Visual Inspect | S |  |  |  |  | Contractor
d. | Excessive back pressure | Test | A |  |  |  |  | Contractor
e. | Exhaust system hangers and supports | Visual Inspect | A |  |  |  |  | Contractor
f. | Flexible exhaust section | Visual Inspect | S |  |  |  |  | Contractor
5 | Battery System
a. | Electrolyte level | Check | W |  |  |  |  | Dayton
b. | Terminals clean and tight | Visual inspect / Check | S |  |  |  |  | Contractor
c. | Remove corrosion, case exterior clean and dry | Visual Inspect / Clean | M |  |  |  |  | Contractor
d. | Specific gravity or state of charge | Test | M |  |  |  |  | Contractor
e. | Charger and charger rate | Visual Inspect | M |  |  |  |  | Contractor
f. | Equalize charge | Check | M |  |  |  |  | Contractor
6 | Electrical System
a. | General inspection | Visual Inspect | W |  |  |  |  | Dayton
b. | Tighten control and power wiring connections | Test | A |  |  |  |  | Contractor
c. | Wire chafing where subject to movement | Visual Inspect / Check | S |  |  |  |  | Contractor
d. | Operation of safeties and alarms | Check / Test | S |  |  |  |  | Contractor
e. | Boxes, panels, and cabinets | Clean | S |  |  |  |  | Contractor
f. | Circuit breakers, fuses Note: Do not break manufacturer's seals or perform internal inspection on these devices. | Visual Inspect / Check / Change / Clean / Test | M |  |  |  |  | Contractor
g. | Calibration of voltage-sensing relays/devices | Check Test | A |  |  |  |  | Contractor
h. | Wire insulation breakdown | Test | 5yr or 500hra |  |  |  |  | Contractor
7 | Prime Mover
a. | General inspection | Visual Inspect | W |  |  |  |  | Dayton
b. | Service air cleaner | Change / Clean | S |  |  |  |  | Contractor
c. | Governor oil level and linkage | Visual Inspect / Check | M |  |  |  |  | Contractor
d. | Change Governor oil | Change | A |  |  |  |  | Contractor
e. | Ignition system - plugs, points, coil, cap, rotor, secondary wire insulation | Visual Inspect / Check / Change / Clean / Test | A |  |  |  |  | Contractor
f. | Operate EPS unloaded | Test (30min) | W for 3-5min |  |  |  |  | Dayton
g | Operate EPS with building load (minimum 50% loaded) | Test (2hr) | M for 15-30min |  |  |  |  | Dayton
h. | Operate EPS with building load (minimum 50% loaded) | Test (4hr) | A for 2hr |  |  |  |  | Dayton
i. | Valve clearance | Test | 3yrs or 500hrsb |  |  |  |  | Contractor
j. | Torque bolts | Test | 3yrs or 500hrsb |  |  |  |  | Contractor
8 | Generator
a. | Brush length, appearance, free to move in holder | Visual Inspect / Check / Clean | W |  |  |  |  | Dayton
b. | Commutator and slip rings | Visual Inspect / Clean | S |  |  |  |  | Contractor
c. | Rotor and stator | Visual Inspect / Clean | A |  |  |  |  | Contractor
d. | Bearing(s) | Visual Inspect / Change | A |  |  |  |  | Contractor
e. | Bearing grease | Check / Change | A |  |  |  |  | Contractor
f. | Exciter | Visual Inspect / Check / Clean | A |  |  |  |  | Contractor
g. | Voltage Regulator | Visual Inspect / Check / Clean | A |  |  |  |  | Contractor
h. | Measure and record resistance readings of windings with insulation tester (Megger) | Test | A |  |  |  |  | Contractor
| Remove generator outlet box cover, inspect stator ouput leads and insulatio for cracking or damage. Check exposed electrical connections for tightness. Check transformers, fuses, capacitors, and lightning arrestors for loose mounting or damage.Check lead wires and electrical connections for proper clearance and spacing. Clean inside of outlet box, air screens, and air baffles. Check machine vibrations and bearing conditions. Regrease optional regreaseable-type bearings. | Check / Clean | 2,000hr |  |  |  |  | Contractor
i. | Top end of the engine - overhaul remove cylinder head and inspect and service combustion chambers | Check / Clean | 4,000hr |  |  |  |  | Contractor
j. | Major overhaul disassemble engine, clean, check and change major parts. Check insulation resistance to gound on all generator windings. Check space heaters for proper operations. Check rotating rectifier connection tightness. Inspect and test fuel injection pump and govenor. | Check / Clean | 8,000hr |  |  |  |  | Contractor
| Remove endbrackets, inspect generator end windings for oil or dirt contamination. Use compressed air and electrical solvent if needed. Inspect the bearing(s) for wear or damage and replace as needed. | Check / Clean | 20,000hr |  |  |  |  | Contractor
| Disassemble generator. Clean generator windings using either compressed air and electrical solvent or degreaser and high pressure hot water wash and then dry windings. Inspect the rotor shaft bearing journals and bracket bearing cavity for wear or scoring. Replace the bearings. | Check / Clean | 30,000hr |  |  |  |  | Contractor
9 | Miscellaneous
a. | General condition of EPSS, any unusual condition of vibration, leakage, noise, temperature, or deterioration | Visual Inspect / Clean | S |  |  |  |  | Contractor
b. | Service room or housing housekeeping | Visual Inspect / Clean | W |  |  |  |  | Dayton
c. | Restore system to automatic operation condition | Visual Inspect | W |  |  |  |  | Dayton
Entire Standby Power System
1 | Generator Hours (at start)
2 | Generator Hours (at end)
3 | Voltage |  |  |  | A-B | B-C | C-A
[5 empty] | A-N | B-N | C-N
4 | Current |  |  |  | A | B | C
5 | Coolant Temperature (after stabilizes)
6 | Exhaust Temperature (after stabilizes)
| a - Every 5 years or 500 hours |  | EPS = Emergency Power Supply
| b - Every 3 years or 500 hours |  | EPSS = Emergency Power Supply System
| c - Every 3 years for 4 hours |  | W, M, S, A |  | = Weekly, Monthly, Semi-annual, Annual
Note on I10: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Responsible party